## List1
ATREA orders | Catalogue number | Outdoor unit Fuji, Fujitsu, General | Model ATREA | Stávající cena v TCV | Cena ATREA | Obj. č. TČ, VZD | Použití v TČ, VZD | Power |  | El. characteristics | [5 empty] | Communication |  | Working conditions |  |  |  | Mechanical specification |  |  |  |  | Noise | Cooling circuit | [7 empty] | Air
|  |  |  | Mělo by odpovídat nákupní ceně |  |  |  | Coolong | Heating | Max. input of cooling | Max. output of heating | Power voltage | Max. power current | Recommended fuses | Power cable Cu | Communication cable Cu | Type of communication | Outdoor temperature |  | Min. temperature of madium - cooling | Max. temperature of medium - heataing | Sizes in mm |  |  | Spacing of consoles in mm | Weight | Distance of 1 m (cooling/heating) | Ø Diameter of Cooper piping - gass | Ø Diameter of Cooper piping - liquid | Max. length of piping | Max. heght difference | Refrigerant filling | Prefilled for length | Refrigerant addition | Oil filling | Air output/power of ventilators | Number of ventilators
[8 empty] | kW | kW | kW | kW | V | A | A | mm2 | mm2 |  | Coolong | Heating | °C | °C | height | wide | depth | depth/wide | kg | dB | mm | mm | m | m | kg | m | g/m | kg | m3/h | -
1 phase units - refrigerant R32 (outdoor unit)
Line
| ROG09KMTA | ROG(AO G)09KMTA | [5 empty] | 2.5 | 2.8 | 1.21 | 1.26 | 230 | 9 | 16 | 3x 2,5 | 3x1,5 | 5 - ROG-KM | -10~46 | -15~24 | 12 | 50 | 541 | 663 | 290 | 330/450 | 23 | 46 | 9.52 | 6.35 | 20 | 15 | 0.6 | 15 | 20 | N/A | 1650 | 1
| ROG12KMTA | ROG(AO G)12KMTA | [5 empty] | 3.4 | 4 | 1.27 | 1.52 | 230 | 9 | 16 | 3x 2,5 | 3x1,5 | 5 - ROG-KM | -10~46 | -15~24 | 12 | 50 | 541 | 663 | 290 | 330/450 | 25 | 50 | 9.52 | 6.35 | 20 | 15 | 0.7 | 15 | 20 | N/A | 1700 | 1
| ROG14KMTA | ROG(AO G)14KMTA | [5 empty] | 4.2 | 5.4 | 1.4 | 1.73 | 230 | 9 | 16 | 3x 2,5 | 3x1,5 | 5 - ROG-KM | -10~46 | -15~24 | 12 | 50 | 542 | 799 | 290 | 330/580 | 31 | 50 | 9.52 | 6.35 | 20 | 15 | 0.85 | 15 | 20 | N/A | 1680 | 1
1 phase units - refrigerant R410 (a set of - outdoord unit, CIM module, temperature sensor)
| KAOU12Ui | ROG(AO G)12LALL | [5 empty] | 3.5 | 4.1 | 1.7 | 2.26 | 230 | 10 | 16 | 3x 2,5 | 3x1,5 | 2 - ROG-L | -10~46 | -15~24 | 12 | 55 | 578 | 790 | 300 | 320/540 | 40 | 47/48 | 9.52 | 6.35 | 25 | 15 | 1.15 | 15 | 20 | N/A | 1780 | 1
| KAOU14Ui | ROG(AO G)14LALL | [5 empty] | 4.3 | 5 | 2.04 | 2.83 | 230 | 12.5 | 16 | 3x 2,5 | 3x1,5 | 2 - ROG-L | -10~46 | -15~24 | 12 | 55 | 578 | 790 | 300 | 320/540 | 40 | 49/49 | 12.7 | 6.35 | 25 | 15 | 1.25 | 15 | 20 | N/A | 1910 | 1
| KAOU18Ui | ROG(AO G)18LBCB | [5 empty] | 5.2 | 6 | 2.04 | 2.83 | 230 | 13.5 | 16 | 3x 2,5 | 3x1,5 | 2 - ROG-L | -10~46 | -15~24 | 12 | 55 | 632 | 799 | 290 | 330/580 | 36 | 50/50 | 12.7 | 6.35 | 25 | 15 | 1.2 | 15 | 20 | N/A | 2380 | 1
| KAOU24Ui | ROG(AO G)24LBCB | [5 empty] | 6.8 | 8 | 2.85 | 3.19 | 230 | 15.7 | 16 | 3x 2,5 | 3x1,5 | 2 - ROG-L | -10~46 | -15~24 | 12 | 55 | 716 | 820 | 315 | 330/600 | 42 | 53/54 | 15.88 | 6.35 | 30 | 15 | 1.5 | 15 | 20 | N/A | 2850 | 1
| KAOC30Ui | ROG(AO G)30LETL | [5 empty] | 8.5 | 10 | 3.88 | 3.88 | 230 | 17 | 20 | 3x 4 | 3x1,5 | 2 - ROG-L | -15~46 | -15~24 | 12 | 55 | 830 | 900 | 330 | 370/650 | 61 | 53/55 | 15.88 | 9.52 | 50 | 30 | 2.1 | 20 | 40 | N/A | 3600 | 1
| KAOU36Ui | ROG(AO G)36LETL | [5 empty] | 9.4 | 11.2 | 4.22 | 4.56 | 230 | 20 | 20 | 3x 4 | 3x1,5 | 2 - ROG-L | -15~46 | -15~24 | 12 | 55 | 830 | 900 | 330 | 370/650 | 61 | 54/55 | 15.88 | 9.52 | 50 | 30 | 2.1 | 20 | 40 | N/A | 3800 | 1
| KAOC45Ui | ROG(AO G)45LETL | [5 empty] | 12.5 | 14 | 4.8 | 4.8 | 230 | 21 | 25 | 3x 4 | 3x1,5 | 2 - ROG-L | -15~46 | -15~24 | 12 | 55 | 1290 | 900 | 330 | 650/370 | 86 | 55/55 | 15.88 | 9.52 | 50 | 30 | 3.35 | 20 | 40 | N/A | 6750 | 2
| KAOU54Ui | ROG(AO G)54LETL | [5 empty] | 13.4 | 16 | 4.77 | 4.69 | 230 | 23.5 | 25 | 3x 4 | 3x1,5 | 2 - ROG-L | -15~46 | -15~24 | 12 | 55 | 1290 | 900 | 330 | 650/370 | 86 | 55/57 | 15.88 | 9.52 | 50 | 30 | 3.35 | 20 | 40 | N/A | 6750 | 2
3 phase units - refrigerant R410 (a set of - outdoord unit, CIM module, temperature sensor)
| KAOC36UiT | ROG(AO G)36LATT | [5 empty] | 10 | 11.2 | 5.12 | 5.12 | 400 | 7.9 | 10 | 5x 2,5 | 3x1,5 | 2 - ROG-L | -15~46 | -15~24 | 12 | 55 | 1290 | 900 | 330 | 650/370 | 104 | 51/53 | 15.88 | 9.52 | 50 | 30 | 3.45 | 30 | 50 | N/A | 6200 | 2
| KAOC45UiT | ROG(AO G)45LATT | [5 empty] | 12.5 | 14 | 5.8 | 5.8 | 400 | 8.9 | 16 | 5x 2,5 | 3x1,5 | 2 - ROG-L | -15~46 | -15~24 | 12 | 55 | 1290 | 900 | 330 | 650/370 | 104 | 54/54 | 15.88 | 9.52 | 50 | 30 | 3.45 | 30 | 50 | N/A | 6750 | 2
| KAOU54UiT | ROG(AO G)54LATT | [5 empty] | 14 | 16 | 6.48 | 6.48 | 400 | 9.9 | 16 | 5x 2,5 | 3x1,5 | 2 - ROG-L | -15~46 | -15~24 | 12 | 55 | 1290 | 900 | 330 | 650/370 | 104 | 55/56 | 15.88 | 9.52 | 50 | 30 | 3.45 | 30 | 50 | N/A | 6900 | 2
| KAOC60UiT | ROG(AO G)60LATT | [5 empty] | 15 | 18 | 7.15 | 7.15 | 400 | 12.5 | 16 | 5x 2,5 | 3x1,5 | 2 - ROG-L | -15~46 | -15~24 | 12 | 55 | 1290 | 900 | 330 | 650/370 | 104 | 56/58 | 15.88 | 9.52 | 75 | 30 | 3.45 | 30 | 50 | N/A | 7300 | 2
| KAOC72UiT | ROG(AO G)72LRLA | [5 empty] | 19 | 22.4 | 6.46 | 6.59 | 400 | 13.3 | 20 | 5x 4,0 | 3x1,5 | 2 - ROG-L | -15~46 | -20~24 | 12 | 55 | 1428 | 1080 | 480 | 688/515,5 | 165 | 55/55 | 25.4 | 12.7 | 100 | 30 | 5.6 | 30 | 110 | N/A | 8400 | 2
| KAOC90UiT | ROG(AO G)90LRLA | [5 empty] | 22 | 27 | 7.7 | 7.8 | 400 | 14.6 | 20 | 5x 4,0 | 3x1,5 | 2 - ROG-L | -15~46 | -20~24 | 12 | 55 | 1428 | 1080 | 480 | 688/515,5 | 174 | 55/57 | 25.4 | 12.7 | 100 | 30 | 7.1 | 30 | 110 | N/A | 9000 | 2
| CIM2 | CIM2 module
| TS-TGL-40 | Temperature sensor TGL-40 DS18B20